## Tabelle1
Fieldbus and availability: Causes of failure - risk and protection
|  |  |  | Protecting component | Power supply | Power supply with redundancy | Trunk cable | Trunk cable, redundant with device coupler | Device coupler, simplex | Device coupler with short-circuit protection | Device coupler with fault isolation | Device coupler with redundant outputs | Spur cable | Field instrument | Field instrument with diagnostics | Field instrument redundant with diagnostics | Surge protection with self-diagnostics | Standard operating procedures | Advanced online physical layer diagnostics
|  |  |  | Performance indicator | 0 | 64 | 0 | 32 | 0 | 32 | 144 | 8 | 0 | 0 | 32 | 40 | 64 | 144 | 192 | Indicates effectiveness of measure
Cause of failure |  | I | F | R | [15 empty] | Comments, own thoughts, other strategies
Components
| Fault in power supply electronics | 3 | 3 | 64 |  | 1
| Fault in device coupler electronics at the spur | 1 | 2 | 8 | [7 empty] | 1
| Instrument fault due to external influences | 2 | 3 | 32 | [10 empty] | 1 | 1
| Instrument fault due to failure of electronics | 2 | 1 | 8 | [11 empty] | 1
General Installation
| Termination incorrect | 1 | 3 | 16 |  |  |  | 1 | [9 empty] | 1 | 1 | Handled by three different solutions
| Electromagnetic interference | 3 | 4 | 128 | [13 empty] | 1 | 1
| Failure of surge protectors | 3 | 3 | 64 | [12 empty] | 1
Wiring at the trunk
| Interruption, e.g., due to cable damage (short-circuit or open circuit) | 3 | 1 | 16 |  |  |  | 1 | [11 empty] | Risk of this happening in hazardous areas is 0!
| Opening contact bounce, e.g., due to vibration | 3 | 1 | 16 | [14 empty] | 1
| Short-circuiting contact bounce | 3 | 1 | 16 | [14 empty] | 1
| Creeping overload, e.g., due to corrosion or moisture | 3 | 1 | 16 | [14 empty] | 1
Wiring at the spur or field instrument
| Solid short circuit | 2 | 3 | 32 | [5 empty] | 1 | 1
| Opening contact bounce, e.g., due to vibration | 2 | 3 | 32 | [6 empty] | 1
| Short-circuiting contact bounce, e.g. live maintenance at a device | 2 | 4 | 64 | [6 empty] | 1
| Creeping overload, e.g., due to corrosion or moisture | 2 | 2 | 16 | [6 empty] | 1
(This line is intentionally not used. Please add additional lines as required above.)
Explanation |  |  |  |  | Notes: all light blue fields are for editing
| Impact, I |  |  |  | 1 | Add lines identifying additional causes of failures
| Very little, operation not in jeopardy (up to $1,000.00 per incident) | 1 |  |  | 2 | Check the Impact and frequency fields to reflect your assessment of risk. (blue fields in columns C and D)
| Additional damage (up to $10,000.00 per incident) | 2 |  |  | 3 | Add or edit any field "in the grid" above. (light blue)
| Serious damage (up to $100,000.00 per incident) | 3 |  |  | 4 | Place a "1" where the measure listed in columns mitigates the risk listed in rows
| Huge damage (up to $1,000,000.00 per incident) | 4 |  |  | 5 | Check for duplicates, e.g., where a risk is controlled by multiple measures (multiple '1' in the same row)
| Frequency, F |  |  |  | 6 | Select the measures that control risk
| Very seldom (you may have heard about it) | 1 |  |  | 7 | Start with highest performance indicators
| Very infrequent (one time in 100 years) | 2
| Infrequent (one time in ten years) | 3 |  |  |  | A separate evaluation of monitoring and control loops can be benefitial.
| Frequent (one time per year) | 4
| Very frequent (ten times per year) | 5
Risk indicator = 2 ^ impact * 2 ^ frequency
Actually, the product should be applied with impact and frequency to the power of ten; however, this would create unnecessarily large risk and performance indicators with no additional insight.